|  | VRF Selector Ultimate 1.5.10.10 |
| --- | --- |

VRF Selection Report

| Project Name |  |  | Date |
| --- | --- | --- | --- |
|  |  |  | 2023/9/26 15:02:15 |
| Project Address |  |  |  |

| Client Name |  |  | Company |  |
| --- | --- | --- | --- | --- |
|  |  |  | Tel. |  |
| Address |  |  |  |  |

# Table Of Contents

1. Abbreviations

2. Project Proposal

2.1 Units

2.2 Branch

2.3 Controller

2.4 Mode Converter

2.5 Piping Length

2.6 Other

3. System

3.1 Outdoor Units Detail

3.2 Indoor Units Detail

3.3 Piping

3.4 System Proposal

4. Piping Diagrams

5. Wiring Diagrams

# 1. Abbreviations

| No. | Abbreviation | Annotation | No. | Abbreviation | Annotation |
| --- | --- | --- | --- | --- | --- |
| 1 | CC | Cooling Capacity | 2 | HC | Heating Capacity |
| 3 | Total CC-IDU | Total Cooling Capacity of IDU | 4 | Total CC-ODU | Total Cooling Capacity of ODU |
| 5 | ESP | External Static Pressure | 6 | Extra Ref. | Additional Refrigerant to the System |
| 7 | DB | Dry Bulb Temperature | 8 | WB | Wet Bulb Temperature |
| 9 | IWT | Inlet Water Temperature | 10 | RH | Relative Humidity |
| 11 | Req TCC-IDU | Required Total Cooling Capacity of IDU | 12 | Req TSC-IDU | Required Total Sensible Cooling Capacity of IDU |
| 13 | Req THC-IDU | Required Total Heating Capacity of IDU | 14 | Rtd CC | Rated Cooling Capacity |
| 15 | Act CC | Actual Cooling Capacity | 16 | Rtd HC | Rated Heating Capacity |
| 17 | Act HC | Actual Heating Capacity | 18 | Rtd PI-C | Rated Input Power for Cooling |
| 19 | Act PI-C | Actual Input Power for Cooling | 20 | Rtd PI-H | Rated Input Power for Heating |
| 21 | Act PI-H | Actual Input Power for Heating | 22 | W×H×D | Width×Height×Depth |
| 23 | FLA | Maximum Current (Full Load Ampere) | 24 | MCA | Minimum Fusing Current (Minimum Circuit Ampere) |
| 25 | MOP | Maximum Overcurrent Protection | 26 | Breaker | Breaker Capacity |
| 27 | Cable Size | Wire Gauge (mm^2) × Number of Wires | 28 | Temp C | Indoor Conditions in Cooling (Dry Bulb Temperature) |
| 29 | Temp H | Indoor Temperature of Indoor Unit Coil (Dry Bulb Temperature) | 30 | Req CC | Required Cooling Capacity |
| 31 | Req SCC | Required Sensible Cooling Capacity | 32 | Act SCC | Actual Sensible Cooling Capacity |
| 33 | Req HC | Required Heating Capacity | 34 | Vertical Dist | Fall with ODU |
| 35 | Design ESP | Design Static Pressure | 36 | Design Airflow | Design Airflow Volume |
| 37 | CC Range | Range of Cooling Capacity | 38 | HC Range | Range of Heating Capacity |
| 39 | AEVR H | Allowable Heat Exchange Volume Range | 40 | Air Flow Range | Suggested Airflow Range |
| 41 | RE(R/E) | Reducer/Expander Pipe | 42 | HG | High Pressure Gas Pipe |
| 43 | LG | Low Pressure Gas Pipe | 44 | LQ | Liquid Pipe |
| 45 | BYx_n_XX | n branch of x branchY-pipe(T: total branch; Number:corresponding branch) |  |  |  |

# 2. Project Proposal

## 2.1 Units

| No. | Model | Description | Quantity | Unit Price | Total Price | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | GMV-VQ72WM/C-F(U) | Ultra Heat GMV6 HR(AHRI) | 1 |  |  |  |
| 2 | GMV-ND07PHS/D-T(U) | High ESP Duct Type(D series) | 9 |  |  |  |

## 2.2 Branch

| No. | Model | Description | Quantity | Unit Price | Total Price | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | FQ01A/A | Branch-Y | 8 |  |  |  |

## 2.3 Reducer/Expander Pipe

| No. | Model | Description | Quantity | Unit Price | Total Price | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | CF344(10/6) | Reducer/Expander Pipe | 1 |  |  |  |
| 2 | CF342(13/10) | Reducer/Expander Pipe | 8 |  |  |  |
| 3 | CF346(16/19) | Reducer/Expander Pipe | 2 |  |  |  |

## 2.4 Controller

| No. | Model | Description | Quantity | Unit Price | Total Price | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | XE7A-24/H | Wired Controller | 18 |  |  | Standard |
| 2 | CE55-24/F(C) | Central Controller | 1 |  |  | Group1 |
| 3 | CE55-24/F(C) | Controller | 1 |  |  | Group1 |

## 2.5 Mode Converter

| No. | Model | Description | Quantity | Unit Price | Total Price | Remark |
| --- | --- | --- | --- | --- | --- | --- |

## 2.6 Piping Length

| No. | Pipe diameter | Total Length | Number Of Elbows | Wall Thickness | Type |
| --- | --- | --- | --- | --- | --- |
|  | inch | ft |  | inch |  |
| 1 | 1/4 | 240 | 0 | ≥1/32 | O |
| 2 | 3/8 | 312 | 0 | ≥1/32 | O |
| 3 | 1/2 | 12 | 0 | ≥1/32 | O |
| 4 | 5/8 | 48 | 0 | ≥3/76 | O |
| 5 | 3/4 | 36 | 0 | ≥3/76 | 1/2H |

## 2.7 Other

| No. | Item | Value | Unit | Description |
| --- | --- | --- | --- | --- |
| 1 | Communication line | 3,237.39 | ft | This value is used as a reference value. |
| 2 | Extra Ref. | 2.77 | Lbs | R410A |

# 3. System

## 3.1 System 1

### 3.1.1 System Proposal

1. Units

| No. | Model | Quantity | Description |
| --- | --- | --- | --- |
| 1 | GMV-VQ72WM/C-F(U) | 1 | Ultra Heat GMV6 HR(AHRI) |
| 2 | GMV-ND07PHS/D-T(U) | 9 | High ESP Duct Type(D series) |

2. Piping Length

| No. | Pipe diameter | Total Length | Number Of Elbows | Wall Thickness | Type |
| --- | --- | --- | --- | --- | --- |
|  | inch | ft |  | inch |  |
| 1 | 1/4 | 240 | 0 | ≥1/32 | O |
| 2 | 3/8 | 312 | 0 | ≥1/32 | O |
| 3 | 1/2 | 12 | 0 | ≥1/32 | O |
| 4 | 5/8 | 48 | 0 | ≥3/76 | O |
| 5 | 3/4 | 36 | 0 | ≥3/76 | 1/2H |

3. Accessories

| No. | Item | Quantity | Unit | Description |
| --- | --- | --- | --- | --- |
| 1 | FQ01A/A | 8 | Pcs. | Branch-Y |
| 2 | CF344(10/6) | 1 | Pcs. | Reducer/Expander Pipe |
| 3 | CF342(13/10) | 8 | Pcs. | Reducer/Expander Pipe |
| 4 | CF346(16/19) | 2 | Pcs. | Reducer/Expander Pipe |
| 5 | XE7A-24/H | 18 | Pcs. | Wired Controller(Standard) |
| 6 | CE55-24/F(C) | 1 | Pcs. | Central Controller |
| 7 | CE55-24/F(C) | 1 | Pcs. | Controller |
| 8 | Communication line | 3,237.39 | ft | This value is used as a reference value. |
| 9 | Extra Ref. | 2.77 | Lbs | R410A |

### 3.1.2 Outdoor Units Detail

| Model |  |  |  | GMV-VQ72WM/C-F(U) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Basic Unit |  |  |  | GMV-VQ72WM/C-F(U) |  |  |  |
| Description |  |  |  | Ultra Heat GMV6 HR(AHRI) |  |  |  |
| Total CC-ODU | Total CC-IDU | Power Supply | Rtd PI-C |  | Act PI-C | Rtd PI-H | Act PI-H |
| kBtu/h | kBtu/h |  | kW |  | kW | kW | kW |
| 72 | 63 | 208/230 3Ph 60Hz | / |  | / | / | / |
| Connection ratio | Req TCC-IDU | Rtd CC | Act CC |  | Req THC-IDU | Rtd HC | Act HC |
| % | kBtu/h | kBtu/h | kBtu/h |  | kBtu/h | kBtu/h | kBtu/h |
| 87.50 | 0 | 72 | 62.96 |  | 0 | 81 | 78.06 |

*Note:"Actual value" refers to the actual capacity or input power corrected according to the design temperature, pipe length and height differential.

| Design Condition | - | DB | WB | RH |
| --- | --- | --- | --- | --- |
|  |  | ℉ | ℉ | % |
| Cooling | Indoor Side | 80.6 | 66.2 | 45.77 |
|  | Outdoor Side | 95 | - | - |
| Heating | Indoor Side | 68 | - | - |
|  | Outdoor Side | 44.6 | 42.8 | 85.36 |

Electrical

| Model | W×H×D | Net Weight | Breaker | Cable Size | FLA | MCA | MOP |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | inch | Lbs | A | sq in | A | A | A |
| GMV-VQ72WM/C-F(U) | 52-3/4×66-1/2×30-1/2 | 750 | 60 | *4 | / | 59.5 | 60 |

### 3.1.3 Indoor Units Detail

1. Normal indoor unit

| Name | Model | Temp C/RH | Temp H | Req CC | Act CC | Req SC | Act SC | Req HC | Act HC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | ℉/% | ℉ | kBtu/h | kBtu/h | kBtu/h | kBtu/h | kBtu/h | kBtu/h |
| Ind 1 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 2 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 3 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 4 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 5 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 6 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 7 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.5 | 0 | 6.18 | 0 | 8.45 |
| Ind 8 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.49 | 0 | 6.18 | 0 | 8.45 |
| Ind 9 | GMV-ND07PHS/D-T(U) | 80.6/45.77 | 68 | 0 | 7.49 | 0 | 6.18 | 0 | 8.45 |

*Note:"Actual value" refers to the actual capacity or input power corrected according to the design temperature, pipe length and height differential.

| Name | Description | Rtd CC | Rtd HC | Controller | Vertical Dist | Design ESP | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | kBtu/h | kBtu/h |  | ft | inWG |  |
| Ind 1 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 2 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 3 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 4 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 5 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 6 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 7 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 8 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |
| Ind 9 | High ESP Duct Type(D series) | 7.5 | 8.5 | XE7A-24/H;XE7A-24/H | 0.00 | 0 |  |

2. Electrical

| Model | W×H×D | Net Weight | ESP | Sound (H/M/L) | Airflow Volume (H/M/L) | Power Supply | Breaker | Cable Size |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | inch | Lbs | inWG | dB(A) | CFM |  | A | sq in |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |
| GMV-ND07PHS/D-T(U) | 27 9/16×11 13/16×27 9/16 | 72 | 0~150 | 35/32/29 | 350/295/245 | 208/230 1Ph 60Hz | 15 | * |

### 3.1.4 Piping

1. Pipes

| Position | Liquid Pipe | Gas Pipe (Low Pressure) | Gas Pipe (High Pressure) | Total Length | Number Of Elbows |
| --- | --- | --- | --- | --- | --- |
|  | inch | inch | inch | ft |  |
| BY8_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY8_P2 | 1/4 | 3/8 | - | 12 | 0 |
| BY7_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY7_P2 | 1/4 | 1/2 | - | 12 | 0 |
| BY6_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY6_P2 | 3/8 | 5/8 | - | 12 | 0 |
| BY5_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY5_P2 | 3/8 | 5/8 | - | 12 | 0 |
| BY4_P1 | 1/4 | 3/8 | - | 132 | 0 |
| BY4_P2 | 3/8 | 5/8 | - | 12 | 0 |
| BY3_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY3_P2 | 3/8 | 5/8 | - | 12 | 0 |
| BY2_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY2_P2 | 3/8 | 3/4 | - | 12 | 0 |
| BY1_P1 | 1/4 | 3/8 | - | 12 | 0 |
| BY1_P2 | 3/8 | 3/4 | - | 12 | 0 |
| MainPipe | 3/8 | 3/4 | - | 12 | 0 |

*Note: High-pressure and low-pressure gas pipes are only applicable to heat recovery units.

2.1 Reducer/Expander Pipe

| Name | Model | R/E Pipe Size | R/E Pipe Size | Diameter of engineering pipe | Position |
| --- | --- | --- | --- | --- | --- |
|  |  | Outside diameter - branch pipe side: inch | Inner diameter - engineering pipe side: inch | inch |  |
| BY8_T_LQ | CF344(10/6) | 3/8 | 1/4 | 1/4 | BY8 ---- BY7_P2 |
| BY8_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY8 ---- BY8_P1 |
| BY7_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY7 ---- BY7_P1 |
| BY6_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY6 ---- BY6_P1 |
| BY5_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY5 ---- BY5_P1 |
| BY4_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY4 ---- BY4_P1 |
| BY3_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY3 ---- BY3_P1 |
| BY2_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY2 ---- BY2_P1 |
| BY2_2_LG | CF346(16/19) | 5/8 | 3/4 | 3/4 | BY2 ---- BY2_P2 |
| BY1_1_LG | CF342(13/10) | 1/2 | 3/8 | 3/8 | BY1 ---- BY1_P1 |
| BY1_2_LG | CF346(16/19) | 5/8 | 3/4 | 3/4 | BY1 ---- BY1_P2 |

2.2 Reducer/Expander Information

| Name | Model | Diameter of branch pipe | Diameter of engineering pipe | Position |
| --- | --- | --- | --- | --- |
|  |  | inch | inch |  |

3. Piping Limitations

| Item |  | Limited Length (≤) |  | Actual Length |  |
| --- | --- | --- | --- | --- | --- |
|  |  | ft |  | ft |  |
| Actual total piping length |  | 39370.08 |  | 324 |  |
| From ODU to the farthest IDU | Actual Length |  | 6496.06 |  | 180 |
|  | Equivalent length |  | 7480.31 |  | 265.48 |
| Length difference between the farthest and the nearest IDU to first indoor branch |  | 1574.8 |  | 156 |  |
| Distance between first indoor branch and the farthest IDU |  | 3543.31 |  | 168 |  |
| Maximum height difference between ODU and IDU | When ODU is installed above IDU |  | 3543.31 |  | 0 |
|  | When ODU is installed below IDU |  | 3543.31 |  | 0 |
| Maximum height difference (h) between IDU and IDU |  | 1181.1 |  | 0 |  |
| Maximum length of the main pipe |  | 3543.31(<) |  | 12 |  |
| Length from IDU to the nearest branch |  | 1574.8 |  | 132 |  |

*Note:

Please refer to the product manual or manual for details.

# 4. Piping Diagrams

The diagram can be copied to paint tool, it can be adjusted photo's size.

## 4. 1 System 1

# 5. Wiring Diagrams

The diagram can be copied to paint tool, it can be adjusted photo's size.

## 5. 1 System 1